## Slide 1
Excellence in Engineering Since 1946

## Slide 2
Strand Associates, Inc.® ( )
Wastewater Treatment Plant Facilities Planning Update
Village of Marathon City Utility Commission and Village Board
April 9, 2020

## Slide 3
Presentation Outline
Background
Phosphorus Compliance
WDNR Compliance Agreement
Updated Facilities Plan
Why are These Improvements Needed?
Capacity of the Proposed Facilities
Treatment Alternatives
Recommended Plan
Other Options
Funding
Schedule

## Slide 4: Background
2012
WPDES Permit
P Compliance
Schedule
2016
Report
Identified P Plan;
Many unknowns
2014 to present
P compliance
alternatives change and evolve
2019
WI River TMDL approved;
WDNR Compliance Agreement
2020
MDV approval; WPDES Permit renewal
2017
Multi-Discharger
Variance approved by EPA;
WPDES permit expired
2010 to 2019
WI River TMDL
Ongoing
2012
2014
2016
2018
2020
2018
Regionalization
Evaluations

## Slide 5: Phosphorus Compliance 2020 Permit Reissuance TP Limit
Assumes 0.26 mgd average WWTP flow
As WWTP flows increase to design flow, concentration limits decrease to meet new TMDL mass limit.
*Chemical Phosphorus Removal (CPR) can be used to meet limit
 | Monthly Permit Limit or Equivalent (mg/L) | Annual lbs TP discharged | Reduction from Current Limit | TP lb Offset And Cost At $55/lb
Current plant | 1.0 | 792 | - | -
TMDL Current Scenario | 0.33 (6-month) | 260 | 67% | 530 lb $29,150
Add Tertiary filtration ~$2.7 million | To <0.2 | 158 | 80% | -
MDV (with watershed project) | 0.80 | 633 | 20% | 475 lb $26,125
TMDL SSC Scenario | 0.73* | 578 | 27% | 214 lb $11,770
DNR-projected P limit was 0.075 mg/L until TMDL was approved

## Slide 6: WDNR Compliance Agreement Schedule
(30 day extension granted)
Compliance Agreement was result of 4 Treatment Facility Overflows (TFOs)

## Slide 7: Updated 2016 Facilities Plan
Develop a plan to provide wastewater treatment capacity for the Village’s existing urban service area through the year 2042 (20 years).
Identify alternatives that can be expanded to accommodate future growth beyond the year 2042.
Identify the most cost-effective alternative to implement in the limited site area with the least significant environmental impacts.
Updated report completed in 2016 with phosphorus compliance planning

## Slide 8
Facility Plan Elements Address Equipment and Processes at the End of Their Useful Life
What You Have
Sections 1, 2, and 3
What You Need
Sections 4, 5, and 6
How Do We Get There?
Section 7
Collection system
Flows and loads
Regulatory requirements
Age/condition
Existing plant performance
Recommended Plan
Sections 8, 9, and 10
Implementation plan
Environmental impact summary
Alternatives evaluation
Public participation

## Slide 9: Why are These Improvements Needed?
Aging equipment/facilities and maintenance
  Most of the current facilities were constructed in 1971 or 1999 (20-50 years old).

## Slide 10: Why are These Improvements Needed?
Inadequate Hydraulic Capacity
  Hydraulic bottlenecks in mixed liquor channel.
  Final clarifiers are undersized.
  Effluent pipe (12-inch) is undersized.

## Slide 11: Why are These Improvements Needed?
Compliance issues
  Treatment facility overflows and compliance agreement with WDNR.
  Lower total phosphorus limit (1.0 mg/L or 1,065 lb/yr to 393 lb/yr TMDL)

## Slide 12
Existing Facilities Have Served Village Well
Digester 1971
Control Building
1971
Control Building Addition
1999
Screening and Grit Removal 1999
Primary Clarifier 1999
Blower Building
1971
Aeration Tanks 1971
Final Clarifiers 1971
Chlorine Contact Tank 1971
UV Disinfection
1999
Sludge Storage Tank 1999
Digester before 1971
BPR Tanks 1999
Primary Clarifier 1971

## Slide 13: What is the Capacity of the Proposed Facilities?
Item | Current Design | Design Year 2042 | 2042 with MC Expansion
Daily Average Flow, mgd | 0.35 | 0.36 | 0.36
Peak Hourly Flow, mgd | 1.63 | 2.20 | 2.20
BOD, lbs/day | 627 | 585 | 627
TSS, lbs/day | 630 | 470 | 492
TP, lbs/day | 15 | 18 | 20
Note: Marathon Cheese data is preliminary.

## Slide 14: Two Biological Treatment Alternatives
WWTP-1 Renovation of Existing Facilities, New Final Clarifiers
WWTP-2 Aero-Mod Treatment Unit
Both alternatives include BPR and two clarifiers
WWTP -1
WWTP -2

## Slide 15: Two Biological Treatment Alternatives Evaluated WWTP 1 – Existing Plant Upgrade
Preliminary Treatment
Primary
Clarification
Biological Treatment with BPR
Final Clarification
Disinfection
Influent
Effluent to Outfall
WAS
Biosolids
Thickening
Biosolids Digestion
Biosolids Storage
RAS
Land Application
Common Item
Biological Treatment Alternatives
Common Item
Common Items
Common Item
Chemical Phosphorus Removal
Common Item

## Slide 16: Two Biological Treatment Alternatives Evaluated WWTP 2 – Aeromod Plant and Common Plant Upgrades
Preliminary Treatment
Influent Pumping
Biological Treatment/BPR
Final Clarification and Aerobic Digestion
Disinfection
Influent
Effluent to Outfall
WAS
Biosolids
Thickening
Biosolids Storage
RAS
Land Application
Common Item
Biological Treatment Alternatives
Common Item
Common Items
Common Item
Chemical Phosphorus Removal
Common Item
AEROMOD:
WWTP-2

## Slide 17: Outfall Modifications Included – Location Request to DNR

## Slide 18: Biological Treatment Alternatives – Opinion of Capital Costs
Alternative | Description | Capital Cost
WWTP-1 | New Blowers, Diffusers, Clarifiers | $7,349,000
WWTP-2 | Aero-Mod Treatment Unit, New Blowers | $6,047,000
Note: Does not include cost for common items of $1,694,000.
Includes Contingencies and Engineering.

## Slide 19: Recommended Plan Proposed Improvements – WWTP-2
Source: Marathon County GIS

## Slide 20: Opinion of Capital Costs
Item | Cost
Influent Screening | $239,000
Screening Room Improvements | $42,000
Grit Removal | $99,000
Influent and Effluent Samplers | $18,000
New Effluent Pipe, Outfall | $87,000
Scum and Drain Pumps | $39,000
Sludge Thickening | $27,000
GBT Feed Pump, TWAS Pumps, WAS Tank Aeration | $111,000
Plant Water System | $57,000
Control Building | $181,000
SCADA-Software, PCs, Lift Station and Water System | $200,000
Aero-Mod Equipment | $992,000
Installation | $205,000
Concrete | $935,000
Excavation and site work | $269,000
Demolition | $200,000
Influent Pumping | $225,000
Chemical Phosphorus Removal | $162,000
Digested Sludge Pumps | $42,000
Disinfection | $246,000
New Control and Blower Building | $195,000
Mechanical | $128,000
Electrical | $327,000
Subtotal | $5,026,000
Contractor GCs (10%) | $503,000
Subtotal Construction Cost Opinion | $5,529,000
Contingencies (25%) and Engineering Services (15%) | $2,212,000
Total Capital Costs | $7,741,000
WWTP-2
Common
Elements

## Slide 21
Contingency Amount Decreases as Definition of Project Increases
Increasing Project Definition
Facility Planning
60% Design
90% Design
Bidding
Construction

## Slide 22: Financial Overview – Wastewater Facilities Plan
Item | Cost with ~96% Parallel Cost
Opinion of Total Project Cost | $7,741,000
CWF Principal Forgiveness Amount | ($858,000)
Parallel Cost Contribution – Marathon Cheese (est) | ($310,000)
Resultant Loan Amount | $6,573,000
Projected Loan Rate (pending market changes) | 1.65%
Estimated Annual Debt Service Payment | $388,500
Debt Coverage Ratio | $39,000
Existing Sewer Utility Revenues | $416,000
Anticipated Reduction in Operating Expenses* | ($30,000)
Debt Retirement | ($124,000)
Future Utility Expenditures with New Debt and Operating Expenses | $689,500
Required Increase in Sewer Utility Revenue** | 66%
*Conservative estimate; savings could be greater for less NG use, less maintenance, fewer components for replacement/repair, etc.
**Rate increase may be phased in until loan repayment starts.

## Slide 23: Other Options – Phasing Project Aero-Mod Option not Practical with Phased Approach Phasing for WWTP-1 Alternative:
Scenario 1 – Fulfill DNR Compliance Agreement + SCADA
  Concept requires vetting with DNR
  Probable Three-Phase Approach
  Phase 1 cost = ~$1.1 million
Scenario 2 – “2-year solution”
  Comply with DNR, fix short-list of highest priority issues
  Two or three-phase approach
  Phase 1 cost = ~$2.7 million, second project in ~5 years
  Full review with Village needed
Scenario 3 – “5-year solution”
  Comply with DNR, fix longer list of high priority issues
  Probable two-phase approach
  Phase 1 cost = ~$5.1 million
  Full review with Village needed

## Slide 24: Phased Project Considerations and Risks
Costs of two projects always greater than one project
  Inefficiencies from duplicated efforts in design, construction management, and permitting
  Double bidding effort
  Contractor’s mobilization and other general conditions
  Inflation of building material and labor costs
Continued maintenance of old equipment
Increased potential for failures, permit violations
Potential for higher interest rates
Potential for loss of principal forgiveness, stimulus funding
Not replacing as much of facility as WWTP-2 alternative
  Increased maintenance and potential for failures in remaining infrastructure

## Slide 25: Phasing is Possible, but Results in Higher Total Project Costs
Estimated Combined Construction Cost = ~$9,900,000
Estimated Construction Cost = ~$9,000,000
WWTP-1 Alternative:

## Slide 26: Funding Options Will be Identified to Minimize Costs to Ratepayers
Clean Water Fund
  Low interest loans – 1.65%, 20 year term
  Grants – Principal Forgiveness, General and Phosphorus Reduction
    Regular PF - 15% project costs up to $750,000
    Phosphorus PF – 50% of parallel cost up to $1 million
  ITA and PERF have been filed; Project is on funding Priority List
  Potential Stimulus funds via COVID-19 stimulus, On Project List
USDA Rural Development (Population < 10,000)
  Low interest loan; loan only rate 2.75%, term variable
  Grants – MHI < state MHI to qualify
    Village MHI $59,028 > state MHI $56,439 (census data)
Percentage of MHI:
  CWF State Fiscal Year (SFY) 2021 MHI for Marathon City = $58,516
  CWF SFY 2021 MHI for Wisconsin = $56,759
  For CWF hardship, MHI < 80% state MHI required
  Rate is 1.1% - 1.2% of MHI vs. 2.0% required for WDNR economic hardship variance

## Slide 27: Sewer Rate Impact
Sewer Rates (Residential):

## Slide 28: Schedule That Includes No Phasing
Task | Schedule Date
Hold Public Hearing on Facilities Plan | TBD
Submit Facilities Plan to WDNR per Compliance Agrmt | After Public Hearing
Begin Design | After Public Hearing
Additional Soil Borings and Survey if needed | After Public Hearing
Submit Drawings and Specifications to WDNR | September 30, 2021
Submit CWFP Loan Application | September 30, 2021
WDNR Plan and Specification Approval | Est December 2021
WDNR Funding List | Est December 2021
Project Bid Date | January 2022
Begin Construction | April 2022
Construction Completion (Projected) | August 30, 2023
Construction Completion (Compliance Agreement) | August 30, 2023

## Slide 30
Excellence in Engineering Since 1946